2024. 1

PosMaster Catalogue

# Contents

1.	PosMaster 모델명 형식	7

1.1.	PosMaster-PLC 모델명	7

1.2.	PosMaster-HMI 모델명	8

2.	PosMaster 라인업	9

3.	PosMaster 주문 방법	11

3.1.	PosMaster-PLC 주문 예시	11

3.2.	PosMaster-HMI 주문 예시	12

3.3.	PosMaster 통합형 주문 예시	13

4.	PosMaster-PLC	14

4.1.	Controller 일반사양	14

4.1.1.	CPU Board 사양	16

4.2.	Power Supply 일반사양	18

4.3.	PCI Cards 일반사양	21

4.3.1.	Ethernet 카드(PCIe) 사양	21

4.3.2.	Profibus-DP 카드 사양	23

4.3.3.	CAN 카드 사양	26

4.3.4.	RS-232/422/485 카드 (2 port) 사양	28

4.3.5.	RS-232/422/485 카드 (4 port) 사양	30

4.3.1.	RS-232/422/485 카드 (8 port) 사양	33

4.4.	Options 일반사양	36

4.4.1.	Fan Kit 사양	36

4.5.	Engineering Work System(EWS) 일반사양	37

4.5.1.	EWS 사양	37

5.	PosMaster-HMI	38

5.1.	H/W 최소사양	38

5.2.	Client 일반사양	39

5.3.	Server 일반사양	40

# Table Contents

[Table 1]	PosMaster 모델 라인업	8

[Table 2]	PosMaster-PLC 모델명 분류	10

[Table 3]	PosMaster-HMI 모델명 분류	12

[Table 4]	Controller 사양_General type	16

[Table 5]	CPU 사양_General type	18

[Table 6]	Power supply 사양	20

[Table 7]	Ethernet cards(PCIe) 사양	23

[Table 8]	Profibus DP Card 사양	25

[Table 9]	CAN Card 사양	28

[Table 10]	RS 232/422/485 Card(2Port) 사양	30

[Table 11]	RS 232/422/485 Card(4Port) 사양	32

[Table 12]	RS 232/422/485 Card(2Port) 사양	34

[Table 13]	FAN Kit 사양	36

[Table 14]	EWS 사양	38

[Table 15]	Controller 사양_Tiny type	39

[Table 16]	CPU 사양_Tiny type	41

[Table 17]	Monitor/Panel 사양	43

[Table 18]	Interface slot 사양	44

[Table 19]	CFast Card 사양	45

[Table 20]	Controller 사양_Modular type	46

[Table 21]	Power 모듈 사양	47

[Table 22]	Serial 모듈 사양	48

[Table 23]	Ethernet 모듈 사양	48

[Table 24]	USB 모듈 사양	49

[Table 25]	H/W 최소사양	51

[Table 26]	Designer 사양_독립형	52

[Table 27]	I/O Server 사양_독립형	53

[Table 28]	Trend Server 사양_독립형	53

[Table 29]	Operation Client 사양_독립형	54

[Table 30]	Trend Client 사양_독립형	54

[Table 31]	Designer 사양_Edge형	55

[Table 32]	I/O Server 사양_Edge형	56

[Table 33]	Client 사양_Edge형	56

# Figure Contents

[Fig. 1]	PosMaster-PLC 모델명 형식	10

[Fig. 2]	PosMaster-HMI 모델명 형식	12

[Fig. 3]	PosMaster-PLC 주문 예시	13

[Fig. 4]	PosMaster-HMI 주문 예시	14

[Fig. 5]	PosMaster-Edge 주문 예시	15

[Fig. 6]	IPC 경제형, 표준형, 고급형, 최고급형(General type) 도면	19

[Fig. 7]	Power Supply 10A 도면	22

[Fig. 8]	Ethernet card 1port, 4port 도면	24

[Fig. 9]	Profibus DP 2port 도면	27

[Fig. 10]	PosMaster-PLC 모델명 형식	29

[Fig. 11]	RS 232/422/485 2port 도면	31

[Fig. 12]	RS 232/422/485 4port 도면	34

[Fig. 13]	RS 232/422/485 8port 도면	36

[Fig. 14]	RS 232/422/485 8port fig.	37

[Fig. 15]	IPC 표준형, 고급형(Tiny type) 도면	42

PosMaster Catalogue

본 카다로그에서는 PosMaster 제품의 라인업과 모델명 형식, 주문 형식을 설명하고, PosMaster-PLC와 HMI의 주요 구성품 사양 및 소프트웨어 기능에 대해서 설명합니다.

PosMaster 모델명 형식

PosMaster-PLC 모델명

PosMaster-PLC의 주문, 시스템 구성 등에 있어서, 각 구성품의 효율적 관리를 위해 다음과 같은 체계에 따라 모델번호를 부여합니다.

PosMaster-PLC 모델명 형식

PosMaster-PLC 모델명 분류

| 구분 | 타입 |
| --- | --- |
| 제품 구분 | • P : PLC, H : HMI, T : TMS |
| 장치 구분 | • C : IPC 모듈 • P : PCI 또는 PCIe 카드 • E : Engineering Work Station |
| IPC 사양 | • ET: 경제형 IPC (Economy) • ST: 표준형 IPC (Standard) • HI : 고급형 IPC (High Performance) • PS : IPC용 Power Supply • FN : IPC용 FAN |
| PCI 사양 | • EN: 이더넷카드, • PD: Profibus-DP카드 • CN : CAN 카드 • RS : RS-232/422/485 카드 |
| 번호 | • 첫번째 자리 : IPC Slot 수 또는 PCI 통신 채널 수 • 두번째 자리 : 버전 (0부터 시작) |

PosMaster-HMI 모델명

PosMaster의 HMI의 모델 번호는 다음과 같이 부여합니다.

PosMaster-HMI 모델명 형식

PosMaster-HMI 모델명 분류

| 구분 | 타입 |
| --- | --- |
| 제품 구분 | • P : PLC, H : HM I, T : TMS |
| 장치 구분 | • S : Server • C : Client |
| Server 사양 | • 01: Tag 1K를 지원 • 03: Tag 3K를 지원 • 06: Tag 6K를 지원 • 10: Tag 10K를 지원 • 60: Tag 60K를 지원 |
| Client 사양 | • 01: Linux용 • 02: Windows용 |
| 제조사 | • DX: 포스코DX 솔루션 |
| 번호 | • 00부터 버전 시작 |

PosMaster 라인업

PosMaster의 PLC와 HMI의 제품 라인업은 아래와 같습니다.

PosMaster-PLC 모델 라인업

| 구분 | 종류 |  | 모델명 | 비고 |
| --- | --- | --- | --- | --- |
| IPC / 부속장치 | • ET: 경제형 IPC (Economy) |  | PMP-CETBR-50 |  |
|  | • ST: 표준형 IPC (Standard) |  | PMP-CSTBR-50 |  |
|  | • HI : 고급형 IPC (High Performance) |  | PMP-CHIBR-50 |  |
|  | • PS : IPC용 Power Supply |  | PMP-CPSBR-00 | PLC용 |
|  |  |  | PMP-CPSWM-00 | TMS용 |
|  | • FN : IPC용 FAN |  | PMP-CFNBR-00 |  |
| PCI | • EN: 이더넷카드 | • Ethernet PCIe 1 포트 | PMP-PENBR-10 |  |
|  |  | • Ethernet PCIe 4 포트 | PMP-PENBR-40 |  |
|  | • PD: Profibus-DP 카드 (PCI 2 포트) |  | PMP-PPDHS-20 |  |
|  | • CN : CAN 카드 (PCI 2 포트) |  | PMP-PCNAV-20 |  |
|  | • RS-232/422/485 카드 | • 시리얼 PCI 2 포트 | PMP-PRSMX-20 |  |
|  |  | • 시리얼 PCI 4 포트 | PMP-PRSMX-40 |  |
|  |  | • 시리얼 PCI 8 포트 | PMP-PRSMX-80 |  |
| EWS | • WS : Engineering Work Station |  | PMP-EWSDX-00 |  |

PosMaster-HMI 모델 라인업

| 구분 | 종류 |  | 모델명 | 비고 |
| --- | --- | --- | --- | --- |
| HMI S/W | • Server | • 1K IO Server | PMH-S01DX-00 |  |
|  |  | • 3K IO Server | PMH-S03DX-00 |  |
|  |  | • 6K IO Server | PMH-S06DX-00 |  |
|  |  | • 10K IO Server | PMH-S10DX-00 |  |
|  |  | • 60K IO Server | PMH-S60DX-00 |  |
|  | • Client | • Linux용 Client | PMH-C01DX-00 |  |
|  |  | • Windows용 Client | PMH-C02DX-00 |  |

PosMaster 주문 방법

PosMaster의 PLC와 HMI 주문방법은 아래와 같은 구성으로 선택하시면 됩니다. 단순한 방식은 예시를 참고하시고, 상세한 내용은 공급사 제품 문의를 통해 확인하시기 바랍니다.

PosMaster-PLC 주문 예시

: 표준형 PLC에 Profibus-DP 통신 인터페이스를 적용하는 경우

- Controller 선택

ᆞPMP-CSTBR-50 → 표준형 PLC

- Power Supply 선택

ᆞPMP-CPSBR-00 → PLC용 전원공급장치 10A

- 통신 인터페이스 선택

ᆞPMP-PPDHS-20 → Profibus-DP(PCI) 2port 카드

- PLC EWS 선택

ᆞ PMP-EWSDX-00 → PLC Engineering Work System

[제품 선택 결과]

| ① |  |  | ② |  |  | ③ |  |  | ④ | PLC EWS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

PosMaster-PLC 주문 예시

PosMaster-HMI 주문 예시

: 독립형 소용량 Server 1종과 Client OS별 각 1종 을 설치하는 경우

- H/W 선택

ᆞ최소 사양 준수할 것 (7.1절H/W 최소사양 참조.)

- Server 선택

ᆞ PMH-S01DX-00 → I/O Server, I/O tag 1K(소용량)

- Client 선택

ᆞ PMH-C01DX-00 → Linux형 (1copy 무료 제공)

ᆞ PMH-C02DX-00 → Windows형

[제품 선택 결과]

| ① | H/W 선택 |  | ② | Server 1종 |  |  | Client 2종 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

PosMaster-HMI 주문 예시

PosMaster 통합형 주문 예시

: Profibus-DP 통신을 장착한 PLC(표준형)에 HMI(1K Tag IO Server와 1 Client)를 통합으로 설치하는 경우

- Controller 선택

ᆞ PMP-CSTBR-50 → 표준형 PLC

- Power Supply 선택

ᆞ PMP-CPSBR-00 → PLC용 전원공급장치, 10A

- Profibus-DP 통신 인터페이스 선택

ᆞ PMP-PPDHS-20 → Profibus-DP(PCI) 2port, PCI

- EWS 선택

ᆞ PMP-EWSDX-00 → PLC Engineering Work System

- 1 K Tag HMI Server 선택

PMH-S01DX-00 → HMI , I/O tag 1K

- Linux용 HMI Client 선택

ᆞ PMH-C01DX-00 → 1 Client 무료제공

[제품 선택 결과]

HMI

Client

HMI

Server

⑥

⑤

PLC EWS

③

④

②

①

PosMaster-Edge 주문 예시

PosMaster-PLC

Controller 일반사양

IPC Controller 사양

| 구분 | 경제형 | 표준형 | 고급형 |
| --- | --- | --- | --- |
| Model Name. | PMP-CETBR-50 | PMP-CSTBR-50 | PMP-CHIBR-50 |
| Figure |  |  |  |
| Certifications |  |  |  |
| CE | Yes |  |  |
| UR | cULus E115267, Industrial control equipment |  |  |
| GOST-R | Yes |  |  |
| CPU | Intel Celeron G3900E | Intel Core i3 6100E | Intel Core i7 6820EQ |
| Memory | 8G | 16G | 32G |
| SSD | 128G | 256G | 512G |
| NVSRAM | 2MB |  |  |
| General Information |  |  |  |
| LEDs | Power, HDD, Link, Run |  |  |
| Cooling | Passive via heat sink and optionally support with an active fan kit |  |  |
| Power button | Yes |  |  |
| Reset button | Yes |  |  |
| Buzzer | Yes |  |  |
| Battery | Renata 950mAh, Lithium ion |  |  |
| Interface |  |  |  |
| COM1 |  |  |  |
| Type | RS232, modem-capable, not electrically isolated |  |  |
| Design | 9-pin, male, DSUB connector |  |  |
| UART | 16550-compatible, 16-byte FIFO |  |  |
| Max. baud rate | 115 kbit/s |  |  |
| USB |  |  |  |
| Quantity | 5 |  |  |
| Type | 4x USB 3.0 (top), 1x USB 2.0 (front) |  |  |
| Design | Type A |  |  |
| Transfer rate | Low speed (1.5 Mbit/s), full speed (12 Mbit/s), high speed (480 Mbit/s), Super Speed (5 Gbit/s) |  |  |
| Current-carrying capacity | Max. 1 A per connection |  |  |
| Ethernet |  |  |  |
| Quantity | 2 |  |  |
| Design | Shielded RJ45 |  |  |
| Transfer rate | 10/100/1000 Mbit/s |  |  |
| Max. baud rate | 1 Gbit/s |  |  |
| Panel/Monitor interface |  |  |  |
| Design | DVI-I |  |  |
| Type | SDL/DVI/Monitor |  |  |
| Inserts |  |  |  |
| PCI/PCIe slots |  |  |  |
| Quantity | 4 PCI slots and 1 PCIe slot |  |  |
| Slide-in drives |  |  |  |
| Quantity | 2 |  |  |
| Add-on UPS slot | Yes |  |  |
| Insert for fan kit | Yes |  |  |
| Electrical characteristics |  |  |  |
| Nominal voltage | 24 VDC ±25%, SELV |  |  |
| Nominal current | Max. 5.5 A |  |  |
| Inrush current | Max. 60 A for <300 μs |  |  |
| Overvoltage Cat. per EN 61131-2 | II |  |  |
| Electrical isolation | Yes |  |  |
| Operation conditions |  |  |  |
| Pollution degree per EN 61131-2 | Pollution degree 2 |  |  |
| Deg. of protection per EN 60529 | IP20 |  |  |

CPU Board 사양

CPU 사양_General type

| 구분 | 경제형 |  | 표준형 |  | 고급형 |  |
| --- | --- | --- | --- | --- | --- | --- |
| Model Name. | PMP-CETBR-50 |  | PMP-CSTBR-50 |  | PMP-CHIBR-50 |  |
| CPU Board |  |  |  |  |  |  |
| Bootloader | Embedded AMI BIOS |  |  |  |  |  |
| Processor |  |  |  |  |  |  |
| Type | Intel Celeron G3900E | Intel Core i3 6100E |  | Intel Core i7 6820EQ |  | Intel Xeon E3 1515MV5 |
| Clock frequency | 2400 MHz | 2700 MHz |  | 2800 MHz |  | 2800 MHz |
| Number of cores | 2 | 2 |  | 4 |  | 4 |
| Architecture | 14 nm |  |  |  |  |  |
| Thermal design power(TDP) | 35 W | 35 W |  | 45 W |  | 45 W |
| Intel Smart Cache | 2 MB | 3 MB |  | 8 MB |  | 8 MB |
| External bus | DMI3, 8 GT/s |  |  |  |  |  |
| Intel 64 architecture | Yes |  |  |  |  |  |
| Intel Turbo Boost Technology | No | No |  | 2.0 |  | 2.0 |
| Intel Hyper-Threading Technology | No | Yes |  | Yes |  | Yes |
| Intel vPro Technology | No | No |  | Yes |  | Yes |
| Intel Virtualization Technology (VT-x) | Yes |  |  |  |  |  |
| Intel Virtualization Technology for Directed I/O(VT-d) | Yes |  |  |  |  |  |
| Enhanced Intel SpeedStep Technology | Yes |  |  |  |  |  |
| Real-time clock |  |  |  |  |  |  |
| Accuracy | At 25°C: typ. 12 ppm (1 second) per day |  |  |  |  |  |
| Battery-backed | Yes |  |  |  |  |  |
| Memory slot |  |  |  |  |  |  |
| Number of memory channels | 2 |  |  |  |  |  |
| Type | DDR4 |  |  |  |  |  |
| Memory size | Max. 32 GB |  |  |  |  |  |
| Max. memory bandwidth | 34.1 GB/s |  |  |  |  |  |
| Graphics |  |  |  |  |  |  |
| Controller | Intel HD Graphics 510 |  | Intel HD Graphics 530 |  | Intel HD Graphics 530 |  |
| Max. dynamic graphics freq. | 950 MHz |  | 950 MHz |  | 1GHz |  |
| Color depth | Max. 32-bit |  | Max. 32-bit |  | Max. 32-bit |  |
| DirectX support | 12 |  | 12 |  | 12 |  |
| OpenGL support | 4.4 |  | 4.4 |  | 4.4 |  |
| Resolution |  |  |  |  |  |  |
| DVI | Resolution up to 1920 x 1200 (WUXGA) |  |  |  |  |  |
| RGB | 350 MHz RAMDAC, resolution up to 2048 x 1536 @ 75 Hz (QXGA) |  |  |  |  |  |
| Display Port | Version 1.2, resolution up to 4K |  |  |  |  |  |
| Mass memory management | 4x SATA |  |  |  |  |  |
| Power management | ACPI 5.0 with battery support |  |  |  |  |  |
| Operation conditions |  |  |  |  |  |  |
| Pollution degree per EN 61131-2 | Pollution degree 2 |  |  |  |  |  |

DIMENSION :

IPC 경제형, 표준형, 고급형 도면

Power Supply 일반사양

Power supply 사양

| 구분 | Power Supply 10A |
| --- | --- |
| Model Name. | PMP-CPSBR-00 |
| Figure |  |
| General Information |  |
| Status display | Green LED (DC OK), threshold value Uout = 21.5 V |
| Isolation voltage |  |
| Input - Output | 4 kV AC (type test), 2 kV AC (routine test) |
| Input - PE | 2 kV AC (type test), 2 kV AC (routine test) |
| Output - PE | 500 VDC (type test) |
| Certification |  |
| CE | Yes |
| UL (cULus) | cULus E123528 Industrial control equipment |
| Input |  |
| Nominal Input voltage | 100 to 240 VAC |
| Input current | AC 85 to 264 V (wide range), 45 to 65 Hz, 300 VAC (temporary) |
| Inrush current limitation | <15 A |
| I2t | 0.7 A2s |
| Power failure bypass | >24 ms (120 VAC), >24 ms (230 VAC) |
| Switch-on time | <1 s (typical) |
| Power factor (cos φ) | 0.99 |
| Discharge current to PE | <3.5 mA |
| Protective circuit | Transient surge protection (varistor) |
| Internal fuse | 6.3 A, slow-blow |
| Required line fuse for line protection | 10 A, 16 A (characteristic B) |
| Input voltage <90 VAC | Derating of the output current: 2.5% per °C |
| Output |  |
| Nominal output Voltage | 24VDC ±1% |
| Output power | 240 W |
| Setting range for output voltage | 22.5 to 29.5 VDC |
| Output current |  |
| -25 to 55°C | 10.0 A |
| >55°C | Derating: 2.5% per °C |
| Current limiting | Approx. 14 A (short circuit) |
| Control deviation | <1% (static load change 10 to 90%), <2% (dynamic load change 10 to 90%), <0.1% (input voltage change ±10%) |
| Rise time | <2 ms (UOUT (10 to 90%)) |
| Max. capacitive load | Unlimited |
| Power back immunity | Max. 35 VDC |
| Efficiency, reliability |  |
| Efficiency | >89% |
| Power dissipation |  |
| Rated load | Max. 30 W |
| No-load operation | Max. 6.7 W |
| Ambient conditions |  |
| Temperature |  |
| Operation | -25 to 70°C (>55°C derating) |
| Storage | -40 to 85°C |
| Relative humidity |  |
| Operation | Max. 95%, non-condensing |
| Mechanical properties |  |
| Housing Material | Sheet metal, galvanized, Side panels: Aluminum |
| Installation | Easy rail mounting (DIN rail NS 35, EN 60715) |
| Dimensions |  |
| Width | 60 mm |
| Height | 130 mm |
| Depth | 152.5 mm |
| Weight | 1400 g |

DIMENSION :

Power Supply 10A 도면

PCI Cards 일반사양

Ethernet 카드(PCIe) 사양

Ethernet 카드(PCIe) 사양

| 구분 | Ethernet 1port | Ethernet 4port |
| --- | --- | --- |
| Model Name. | PMP-PENBR-10 | PMP-PENBR-40 |
| Figure |  |  |
| Diagnostics |  |  |
| Data transfer | Yes, using LED status indicators |  |
| Certifications |  |  |
| CE | Yes |  |
| UL | cULus E115267, Industrial control equipment |  |
| EAC | Product family certification |  |
| Interface |  |  |
| System Bus Type | PCIe |  |
| Ethernet |  |  |
| Quantity | 1 | 4 |
| Controller | Intel I210 | Intel I350 |
| Variant | Shielded RJ45 |  |
| Transfer rate | 10/100/1000 Mbit/s |  |
| Line length | Max. 100 m between two stations (segment length) |  |
| Electrical properties |  |  |
| Power consumption | 1W | 4W |
| Operation conditions |  |  |
| Pollution degree per EN61131-2 | Pollution degree 2 |  |
| Ambient conditions |  |  |
| Temperature |  |  |
| Operation | 0 to 55°C |  |
| Storage | -20 to 60°C |  |
| Relative humidity |  |  |
| Operation | 5 to 90%, non-condensing |  |
| Storage | 5 to 95%, non-condensing |  |
| Vibration |  |  |
| Operation (continuous) | 2 to 9 Hz: 1.75 mm amplitude / 9 to 200 Hz: 0.5 g |  |
| Operation (occasional) | 2 to 9 Hz: 3.5 mm amplitude / 9 to 200 Hz: 1 g |  |
| Storage | 2 to 8 Hz: 7.5 mm amplitude / 8 to 200 Hz: 2 g / 200 to 500 Hz: 4 g |  |
| Shock |  |  |
| Operation | 15 g, 11 ms |  |
| Storage | 30 g, 6 ms |  |
| Elevation |  |  |
| Operation | -300 to 3000 m above sea level |  |

DIMENSION :

Ethernet 카드 (1 port, 4 port) 도면

Profibus-DP 카드 사양

Profibus DP 카드 사양

| 구분 | Profibus DP 2Port |
| --- | --- |
| Model Name. | PMP-PDPHS-20 |
| Figure |  |
| Description | Dual-channel PC card PCI, 2port, CIFX 50-2DP PROFIBUS DP-Master/PROFIBUS DP-Master |
| Communication Controller | netX 100 processor |
| Integrated Memory |  |
| RAM | 8 MB SDRAM |
| FLASH | 4 MB serial Flash EPROM |
| System Interface |  |
| Bus Type | PCI |
| Transmission Rate | 33 MHz |
| Data Access | DPM or DMA (Direct Memory Access) |
| Data width | 32-Bit |
| Communication 1,2 |  |
| Communication standard | PROFIBUS |
| Interface type | RS-485, isolated |
| Isolation voltage | 1000VDC(tested for minute) |
| Connector | D-Sub, female, 9-pin |
| Power supply |  |
| Supply voltage | +3.3VDC±5% |
| Max. current at 3.3V(typically) | 700mA |
| Connector | Via PCI bus |
| Displays |  |
| LED display | SYS : System status LED COM 0 : LED Communication status 0(duo LED) for CH1 COM 1 : LED Communication status 0(duo LED) for CH2 |
| Operating element |  |
| Rotary switch slot number(card ID) | To set the slot number(card ID) |
| Permitted ambient conditions |  |
| Operating temperature range | -10 °C ... +70 °C(Air flow during measurement:0.5m/s) |
| Storage temperature range | -10 °C ... +70 °C |
| Humidity | 10% ... 90% relative humidity, no condensation permitted |
| Environment | For UL compliant usage : The device must be used in a pollution degree 2 environment. |
| Device |  |
| Dimensions(LⅩWⅩH) | 120Ⅹ94.5Ⅹ18.5mm |
| Mounting/Installation | PCI slot(3.3V) |
| Configuration |  |
| Configuration software | SYCON.net |
| Conformity |  |
| RoHS | Yes |
| Conformance with EMC directives |  |
| CE sign | Yes |
| Emission | ᆞEN 55011:2009 + A1:2010, CISPR 11:2009, Class A (Radio disturbance characteristics - Limits and methods of measurement) |
| Immunity | ᆞEN 61000-4-2:2009 (Electrostatic discharge test) ᆞEN 61000-4-3:2006 + A1:2008 + A2:2010 (Radiated, radio-frequency, electromagnetic field test) ᆞEN 61000-4-4:2004 + A1:2010 (Burst Electrical fast transients/burst test) ᆞEN 61000-4-5:2006 (Surge test) ᆞEN 61000-4-6:2009 (to conducted disturbances, induced by radio- frequency fields) ᆞEN 61000-4-8:2010 (power frequency magnetic field test) ᆞEN 61000-6-2:2005 + B1:2011 (for industrial environments) |
| UL certification |  |
| UL | The device is certified according to UL 508. |
| UL file | UL-File-Nr. E221530 |

DIMENSION :

Profibus DP 카드 (2 port) 도면

CAN 카드 사양

CAN 카드 사양

| 구분 | CAN 2port |
| --- | --- |
| Model Name. | PMP-PCNAV-20 |
| Figure |  |
| Description | 2-port CAN Bus Universal PCI Card with Isolation Protection, PCI-1680U |
| System Bus Type | PCI |
| Certification |  |
| CE | Yes |
| FCC | Yes |
| Communications |  |
| Connectors Type | DB9, male |
| Ports | 2 |
| CAN Controller | NXP SJA-1000 |
| CAN Transceiver | NXP TJA1051T |
| Signal Support | CAN_H, CAN_L |
| Protocol | CAN 2.0 A/B |
| Data Transfer Rate | Programmable up to 1 Mbps |
| CAN Frequency | 16MHz |
| Protection |  |
| Isolation Protection | 2.5 KVdc |
| Ports | 2 |
| Environment |  |
| Power Consumption | 3.3 V @ 600 mA |
| Operational Temperature | 0 ~ 70°C (32 ~ 158°F) |
| Storage Temperature | -40 ~ 85 °C (-40 ~ 185 °F) |
| Operating Humidity | 5 ~ 95% relative humidity, non-condensing |

DIMENSION :

168

111

CAN 카드 (2 Port) 도면

RS-232/422/485 카드 (2 port) 사양

RS 232/422/485 카드 (2 Port) 사양

| 구분 | RS 232/422/485 카드 2 port |
| --- | --- |
| Model Name. | PMP-PRSMX-20 |
| Figure |  |
| Description | 2port RS-232/422/485 Universal PCI serial board, CP-112UL |
| Serial Interface |  |
| Comm. Controller | MU860(16C550C compatible) |
| Bus | 32-bit Universal PCI |
| Connector | DB25 female |
| FIFO | 128bytes |
| Max. No. of Board per PC | 8 |
| No. of Ports | 2 |
| Serial Standards | RS-232, RS-422, RS-485 |
| Baud-rate | 50 bps to 921.6kbps |
| Data Bits | 5, 6, 7, 8 |
| Parity | None, Even, Odd, Space, Mark |
| Flow Control | None, RTS/CTS, XON/XOFF |
| Isolation | CP-112UL-I Series: 2kV |
| Serial Signal |  |
| RS-232 | TxD, RxD, RTS, CTS, TR, DSR, DCD, GND |
| RS-422 | Tx+, Tx-, Rx+, Rx-, RTS+, RTS-, CTS+, CTS-, GND |
| RS-485-4w | Tx+, Tx-, Rx+, Rx-, GND |
| RS-485-2w | Data+, Data-, GND |
| Power Parameters |  |
| Input Current | CP-112UL : 175mA, 5VDC (CP-112UL-I) : 290mA, 5VDC |
| Physical Characteristics |  |
| Dimensions | 64.4 Ⅹ 120mm(2.53 Ⅹ 4.72 in) |
| LED Interface |  |
| LED indicators | Built-in Tx, Rx LEDs for each port |
| Operation | 0 to 55°C |
| Environmental Limit |  |
| Operation Temperature | Standard Models: 0 to 55°C (32 to 131°F) Wide Temp. Models: -40 to 85°C (-40 to 185°F) |
| Storage Temperature (package included) | -40 to 85°C (-40 to 185°F) |
| Ambient Relative Humidity | 5 to 95% (non-condensing) |
| Standards & Certifications |  |
| EMC | EN 55032/35 |
| EMS | EC 61000-4-2 ESD: Contact: 4 kV; Air: 8 kV IEC 61000-4-3 RS: 80 MHz to 1 GHz: 3 V/m IEC 61000-4-4 EFT: Power: 1 kV; Signal: 0.5 kV IEC 61000-4-5 Surge: Power: 2 kV IEC 61000-4-6 CS: 150 kHz to 80 MHz: 3 V/m; Signal: 3 V/m |
| Green Product | RoHS, CRoHS, WEEE |
| Serial Cable |  |
| Figure |  |
| Description | 2port RS-232/422/485 serial cable, CBL-M25M9x2-50 |
| Connector |  |
| Board-side Connector | DB25(male) x 1 |
| Device-side Connector | DB9(male) x 2 |
| Physical Characteristics |  |
| Cable Length | 50cm(19.69in) |

DIMENSION :

RS 232/422/485 카드 (2 port) 도면

RS-232/422/485 카드 (4 port) 사양

RS 232/422/485 카드 (4 Port) 사양

| 구분 | RS 232/422/485 카드 4 port |
| --- | --- |
| Model Name. | PMP-PRSMX-40 |
| Figure |  |
| Description | 4port RS-232/422/485 Universal PCI serial board, CP-114UL |
| Serial Interface |  |
| Comm. Controller | MU860(16C550C compatible) |
| Bus | 32-bit Universal PCI |
| Connector | DB44 female |
| FIFO | 128bytes |
| Max. No. of Board per PC | 8 |
| No. of Ports | 4 |
| Serial Standards | RS-232, RS-422, RS-485 |
| Baud-rate | 50 bps to 921.6kbps |
| Data Bits | 5, 6, 7, 8 |
| Stop Bits | 1, 1.5, 2 |
| Parity | None, Even, Odd, Space, Mark |
| Flow Control | None, RTS/CTS, XON/XOFF |
| Isolation | CP-114UL-I Series: 2kV |
| Serial Signal |  |
| RS-232 | TxD, RxD, RTS, CTS, TR, DSR, DCD, GND |
| RS-422 | Tx+, Tx-, Rx+, Rx-, RTS+, RTS-, CTS+, CTS-, GND |
| RS-485-4w | Tx+, Tx-, Rx+, Rx-, GND |
| RS-485-2w | Data+, Data-, GND |
| Power Parameters |  |
| Input Current | CP-114UL : 320mA, 5VDC (CP-114UL-I) : 465mA, 5VDC |
| Physical Characteristics |  |
| Dimensions | 64.4ⅹ120mm(2.53ⅹ4.72 in) CP-114UL-I Series: 64.4 x 130 mm (2.53 x 5.12 in) |
| LED Interface |  |
| LED indicators | Built-in Tx, Rx LEDs for each port |
| Operation | 0 to 55°C |
| Environmental Limit |  |
| Operation Temperature | Standard Models: 0 to 55°C (32 to 131°F) Wide Temp. Models: -40 to 85°C (-40 to 185°F) |
| Storage Temperature (package included) | -40 to 85°C (-40 to 185°F) |
| Ambient Relative Humidity | 5 to 95% (non-condensing) |
| Standards & Certifications |  |
| EMC | EN 55032/35 |
| EMI | CISPR 32, FCC Part 15B Class B |
| EMS | All models: EC 61000-4-2 ESD: Contact: 4 kV; Air: 8 kV IEC 61000-4-3 RS: 80 MHz to 1 GHz: 3 V/m CP-114UL-I : IEC 61000-4-4 EFT: Power: 1 kV; Signal: 0.5 kV IEC 61000-4-5 Surge: Power: 2 kV IEC 61000-4-6 CS: 150 kHz to 80 MHz: 3 V/m; Signal: 3 V/m IEC 61000-4-8 |
| International Approval | CP-114UL-DB9M: KC |
| Green Product | RoHS, CRoHS, WEEE |
| Serial Cable |  |
| Figure |  |
| Description | 4port RS-232/422/485 serial cable, CBL-M44M9x4-50 |
| Connector |  |
| Board-side Connector | DB44(male) x 1 |
| Device-side Connector | DB9(male) x 4 |
| Physical Characteristics |  |
| Cable Length | 50cm(19.69in) |

DIMENSION :

RS 232/422/485 카드 (4 port) 도면

    - RS-232/422/485 카드 (8 port) 사양

RS 232/422/485 카드 (8 Port) 사양

| 구분 | RS 232/422/485 카드 8 port |
| --- | --- |
| Model Name. | PMP-PRSMX-80 |
| Figure |  |
| Description | 8port RS-232/422/485 Universal PCI serial board, CP-118U |
| Serial Interface |  |
| Comm. Controller | MU860(16C550C compatible) |
| Bus | 32-bit Universal PCI |
| Connector | DB62 female |
| FIFO | 128bytes |
| Max. No. of Board per PC | 8 |
| No. of Ports | 8 |
| Serial Standards | RS-232, RS-422, RS-485 |
| Baud-rate | 50 bps to 921.6kbps |
| Data Bits | 5, 6, 7, 8 |
| Stop Bits | 1, 1.5, 2 |
| Parity | None, Even, Odd, Space, Mark |
| Flow Control | None, RTS/CTS, XON/XOFF |
| Isolation | CP-118U-I Series: 2kV |
| Serial Signal |  |
| RS-232 | TxD, RxD, RTS, CTS, TR, DSR, DCD, GND |
| RS-422 | Tx+, Tx-, Rx+, Rx-, RTS+, RTS-, CTS+, CTS-, GND |
| RS-485-4w | Tx+, Tx-, Rx+, Rx-, GND |
| RS-485-2w | Data+, Data-, GND |
| Power Parameters |  |
| Input Current | 300mA, 5VDC |
| Physical Characteristics |  |
| Dimensions | 82ⅹ135mm(3.22ⅹ5.31 in) |
| LED Interface |  |
| LED indicators | Built-in Tx, Rx LEDs for each port |
| Operation | 0 to 55°C |
| Environmental Limit |  |
| Operation Temperature | Standard Models: 0 to 55°C (32 to 131°F) Wide Temp. Models: -40 to 85°C (-40 to 185°F) |
| Storage Temperature (package included) | -40 to 85°C (-40 to 185°F) |
| Ambient Relative Humidity | 5 to 95% (non-condensing) |
| Standards & Certifications |  |
| EMC | EN 55032/35 |
| EMI | CISPR 32, FCC Part 15B Class B |
| EMS | EC 61000-4-2 ESD: Contact: 4 kV; Air: 8 kV IEC 61000-4-3 RS: 80 MHz to 1 GHz: 3 V/m |
| Green Product | RoHS, CRoHS, WEEE |
| Serial Cable |  |
| Figure |  |
| Description | 8port RS-232/422/485 serial cable, CBL-M462M9x8-100 |
| Connector |  |
| Board-side Connector | DB62(male) x 1 |
| Device-side Connector | DB9(male) x 8 |
| Physical Characteristics |  |
| Cable Length | 100cm(3.3ft) |

DIMENSION :

RS 232/422/485 카드 (8 port) 도면

  - Options 일반사양

    - Fan Kit 사양

FAN Kit 사양

| 구분 | FAN Kit |
| --- | --- |
| Model Name. | PMP-CFNBR-00 |
| Figure |  |
| Certification |  |
| CE | Yes |
| UL | cULus E115267, Industrial control equipment |
| General spec. |  |
| Number of fans | 4 (1x 50x50x15, 3x 70x70x15) |
| Speed | Max. 5000 ±10% rpm (50x50x15) Max. 2200 ±250 rpm (70x70x15) |
| Noise level | 33.5 dB(A) (50x50x15) 28.3 dB(A) (70x70x15) |
| Service life | 100,000 hours at 40°C (50x50x15) 100,000 hours at 40°C (70x70x15) |

DIMENSION :

210mm

240.75mm

25mm

IPC 하부 장착용 FAN

  - Engineering Work System(EWS) 일반사양

EWS 사양

EWS 사양

| 구분 | EWS |
| --- | --- |
| Model Name. | PMP-EWSDX-00 |
| HW spec. |  |
| CPU | Intel i5 or i7 Quad Core 3 GHz 이상 |
| RAM | RAM 4GB 이상 |
| Interface | Ethernet(RJ45) |
| Storage | 60GB 이상 |
| OS |  |
| Windows | Windows 7 / 8 / 10, 64Bit |
| Software |  |
| 기본 | Codesys_64_ X.X.X.X.exe (Install Shield) |
| Plug-In | PosMaster-EWS-X.X.X.X.Package ( X.X.X.X : 버전) |
| 주요 기능 |  |
| 프로젝트 관리 | 프로젝트 생성, 저장(압축), 백업, 온라인 전송 기능 등 외부문서 저장, 인쇄, 보호 기능 등 |
| 프로그래밍 | 주석 처리, 변수 선언, 데이터 타입, I/O Address Mapping 등 POU 구성, 프로그램 작성, 컴파일, Debugging 등 |
| 운영 및 모니터링 | 시스템 설정, 운전, 모니터링 기능 |

PosMaster-HMI

H/W 최소사양

H/W 최소사양

| 구분 | 소용량 | 중용량 | 대용량 |
| --- | --- | --- | --- |
| CPU(GHz) | 2.8 | 2.8 | 2.8 |
| CPU Core | 4 | 8 | 20 |
| Memory(GB) | 32 | 64 | 128 |
| Storage(GB) | 500 | 1,000 | 2,000,000 |
| Network(Mbps) | 1,000 | 1,000 | 1,000 |

※ Trend Data 저장항목 및 저장기간에 따라 Storage 용량을 선정해야 합니다.

Client 일반사양

Client 사양_독립형

| 구분 | 사양 |
| --- | --- |
| Model Name. | PMH-C01DX-00 , PMH-C02DX-00 |
| Tag |  |
| I/O Tag | 60,000 (독립형) , 4,000(통합형) |
| Trend Tag | 20,000(독립형) , 800(통합형) |
| 주요 기능 |  |
| 화면 편집기 | Move, Resize, Copy, Paste, Clone, Delete, Undo/Redo 기능 Drag & Drop 방식 지원 Multiple Widget 선택 및 정렬 기능 Zoom In/Out, Guide, Order 변경 기능 Orientation 변경, Group 기능 |
| Widget Palette | Graphic, Monitor, Control, Layout, 기타 Widget |
| Widget Behavior | Macro, Action, Rule 기능 |
| Tag Manager | Tag 등록 및 관리 기능 |
| Data Agent Manager | PLC 통신 Interface 등록 및 관리 기능 |
| Alarm Manager | Alarm 등록 및 관리 기능 |
| Trend Manager | Trend 등록 및 관리 기능 |
| Log Viewer | Log 이력 설정 및 검색 기능 |
| Symbol Factory | 사용자 Symbol 등록 및 관리 기능 제공 |
| Script | Javascript, Python 언어 지원 |
| OS |  |
| Windows / Linux | Windows 10 / Linux LOS (Based on Ubuntu) 20.04 , 22.04 중에서 선택 |

Server 일반사양

I/O Server 사양_독립형

| 구분 | 소용량 | 중용량 | 대용량 |
| --- | --- | --- | --- |
| Model Name. | PMH-S01DX-00 | PMH-S06DX-00 PMH-S10DX-00 | PMH-S60DX-00 |
| Tag |  |  |  |
| I/O Tag | 4,000 | 6,000 / 10,000 | 60,000 |
| PLC Interfaces |  |  |  |
| Modbus | Modbus TCP Client |  |  |
| OPC | OPC UA Client |  |  |
| S7 | S7 |  |  |
| Melsec | MC protocol |  |  |
| 주요 기능 |  |  |  |
| I/O | I/O Tag List를 손쉽게 등록 및 관리 손쉬운 통신Device 연결 설정 |  |  |
| Alarm | Alarm Tag 등록 및 관리 Alarm Log 저장지원 |  |  |
| Trend | Trend Tag 등록 및 관리 Trend 저장 지원 특정기간 Trend Data(엑셀파일)등 다양한 형태로 출력 보고서 출력 기능 |  |  |
| OS |  |  |  |
| Linux | LOS (Based on Ubuntu) 20.04 , 22.04 |  |  |